## _smry
| min | max | depths | dep_dmg | dmg_mono | dep_mono | desc_asset | plot_group | plot_f
UtilFlty_PDFLT_004 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE |  | g1 | TRUE
UtilFlty_PWTL_007 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Large Gravity or Open Treatment Plant (> 200 MGD) | g1 | TRUE
UtilFlty_PWTM_008 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Medium Gravity or Open Treatment Plant (50-200 MGD) | g1 | TRUE
UtilFlty_PWTS_009 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Small Gravity or Open Treatment Plant (<50 MGD) | g1 | TRUE
UtilFlty_PWTO_010 | 0 | 15 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 3.0, 0.6096: 4.0, 0.9144: 5.0, 1.2192: 9.0, 1.524: 12.0, 1.8288: 15.0, 2.1336: 15.0, 2.4384: 15.0, 2.7432: 15.0, 3.048: 15.0} | TRUE | TRUE | Open Treatmet Plant Less than Average Damage (All) | g1 | TRUE
UtilFlty_PWTO_011 | 0 | 45 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 8.0, 0.6096: 12.0, 0.9144: 15.0, 1.2192: 26.0, 1.524: 36.0, 1.8288: 45.0, 2.1336: 45.0, 2.4384: 45.0, 2.7432: 45.0, 3.048: 45.0} | TRUE | TRUE | Open Treatment Plant Greater than Average Damage (All) | g1 | TRUE
UtilFlty_PWTL_012 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Large Closed or Pressure Treatment Plant (>200 MGD) | g1 | TRUE
UtilFlty_PWTM_013 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Medium Closed or Pressure Treatment Plant (50-200 MGD) | g1 | TRUE
UtilFlty_PWTS_014 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Small Closed or Pressure Treatment Plant (<50 MGD) | g1 | TRUE
UtilFlty_PWTC_015 | 0 | 20 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 1.0, 0.9144: 3.0, 1.2192: 8.0, 1.524: 15.0, 1.8288: 20.0, 2.1336: 20.0, 2.4384: 20.0, 2.7432: 20.0, 3.048: 20.0} | TRUE | TRUE | Closed Treatment Plant Less than Average Damage (All) | g1 | TRUE
UtilFlty_PWTC_016 | 0 | 60 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.0, 0.6096: 3.0, 0.9144: 8.0, 1.2192: 23.0, 1.524: 45.0, 1.8288: 60.0, 2.1336: 60.0, 2.4384: 60.0, 2.7432: 60.0, 3.048: 60.0} | TRUE | TRUE | Closed Treatment Plant Greater than Average Damage (All) | g1 | TRUE
UtilFlty_PPPL_017 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Large Pumping Plant Below Grade (>50 MGD) | g1 | TRUE
UtilFlty_PPPM_018 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Medium Pumping Plant Below Grade (10 - 50 MGD) | g1 | TRUE
UtilFlty_PPPS_019 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Small Pumping Plant Below Grade (<10 MGD) | g1 | TRUE
UtilFlty_PPPL_020 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Large Pumping Plant Above Grade (> 50MGD) | g1 | TRUE
UtilFlty_PPPM_021 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Medium Pumping Plant Above Grade (10 - 50 MGD) | g1 | TRUE
UtilFlty_PPPS_022 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Small Pumping Plant Above Grade (<10 MGD) | g1 | TRUE
UtilFlty_PCVS_023 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 40.0, 0.6096: 40.0, 0.9144: 40.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Control Vaults and Control Stations | g1 | TRUE
UtilFlty_PSTAS_024 | 0 | 0 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 0.0, 1.524: 0.0, 1.8288: 0.0, 2.1336: 0.0, 2.4384: 0.0, 2.7432: 0.0, 3.048: 0.0} | TRUE | TRUE | Elevated Tanks | g1 | TRUE
UtilFlty_PSTBC_025 | 0 | 5 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 5.0, 1.524: 5.0, 1.8288: 5.0, 2.1336: 5.0, 2.4384: 5.0, 2.7432: 5.0, 3.048: 5.0} | TRUE | TRUE | Buried Concrete Tank | g1 | TRUE
UtilFlty_PSTGC_026 | 0 | 0 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 0.0, 1.524: 0.0, 1.8288: 0.0, 2.1336: 0.0, 2.4384: 0.0, 2.7432: 0.0, 3.048: 0.0} | TRUE | TRUE | At Grade Concrete Tank | g1 | TRUE
UtilFlty_PSTGS_027 | 0 | 0 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 0.0, 1.524: 0.0, 1.8288: 0.0, 2.1336: 0.0, 2.4384: 0.0, 2.7432: 0.0, 3.048: 0.0} | TRUE | TRUE | At Grade Steel Tank | g1 | TRUE
UtilFlty_PSTGW_028 | 0 | 0 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 0.0, 1.524: 0.0, 1.8288: 0.0, 2.1336: 0.0, 2.4384: 0.0, 2.7432: 0.0, 3.048: 0.0} | TRUE | TRUE | At Grade Wood Tank | g1 | TRUE
UtilFlty_PWE_029 | 0 | 30 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 20.0, 1.524: 25.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 30.0} | TRUE | TRUE | Wells | g1 | TRUE
UtilFlty_WLSL_030 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Large Lift Station Dry Well (>50 MGD) | g1 | TRUE
UtilFlty_WLSL_031 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Large Lift Station Wet Well (>50 MGD) | g1 | TRUE
UtilFlty_WLSL_032 | 0 | 10 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 10.0, 1.524: 10.0, 1.8288: 10.0, 2.1336: 10.0, 2.4384: 10.0, 2.7432: 10.0, 3.048: 10.0} | TRUE | TRUE | Large Lift Station Submersible (>50 MGD) | g1 | TRUE
UtilFlty_WLSM_033 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Medium Lift Station Dry Well (10 - 50 MGD) | g1 | TRUE
UtilFlty_WLSM_034 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Medium Lift Station Wet Well (10 - 50 MGD) | g1 | TRUE
UtilFlty_WLSM_035 | 0 | 10 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 10.0, 1.524: 10.0, 1.8288: 10.0, 2.1336: 10.0, 2.4384: 10.0, 2.7432: 10.0, 3.048: 10.0} | TRUE | TRUE | Medium Lift Station Submersible (10 - 50 MGD) | g1 | TRUE
UtilFlty_WLSS_036 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Small Lift Station Dry Well (<10 MGD) | g1 | TRUE
UtilFlty_WLSS_037 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Small Lift Station Wet Well (<10 MGD) | g1 | TRUE
UtilFlty_WLSS_038 | 0 | 10 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 10.0, 1.524: 10.0, 1.8288: 10.0, 2.1336: 10.0, 2.4384: 10.0, 2.7432: 10.0, 3.048: 10.0} | TRUE | TRUE | Small Lift Station Submersible (<10 MGD) | g1 | TRUE
UtilFlty_WWTL_039 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Large Wastewater Treatment Plant (>200 MGD) | g1 | TRUE
UtilFlty_WWTA_040 | 0 | 60 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 8.0, 0.6096: 12.0, 0.9144: 15.0, 1.2192: 26.0, 1.524: 36.0, 1.8288: 45.0, 2.1336: 45.0, 2.4384: 45.0, 2.7432: 45.0, 3.048: 60.0} | TRUE | TRUE | Wastewater Treatment Plants Greater than Average Damage (All) | g1 | TRUE
UtilFlty_WWTA_041 | 0 | 20 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 3.0, 0.6096: 4.0, 0.9144: 5.0, 1.2192: 9.0, 1.524: 12.0, 1.8288: 15.0, 2.1336: 15.0, 2.4384: 15.0, 2.7432: 15.0, 3.048: 20.0} | TRUE | TRUE | Wastewater Treatment Plants Less than Average Damage (All) | g1 | TRUE
UtilFlty_WWTM_042 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Medium Wastewater Treatment Plant (50 - 200 MGD) | g1 | TRUE
UtilFlty_WWTS_043 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Small Wastewater Treatment Plant (<50 MGD) | g1 | TRUE
UtilFlty_WWCV_044 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 40.0, 0.6096: 40.0, 0.9144: 40.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Wastewater Control Vaults and Control Stations | g1 | TRUE
UtilFlty_WDFLT_045 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 5.0, 0.6096: 8.0, 0.9144: 10.0, 1.2192: 17.0, 1.524: 24.0, 1.8288: 30.0, 2.1336: 30.0, 2.4384: 30.0, 2.7432: 30.0, 3.048: 40.0} | TRUE | TRUE | Default Wastewater Facility | g1 | TRUE
UtilFlty_ODFLT_048 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Default Oil Facility | g1 | TRUE
UtilFlty_OPP_049 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Oil Pumping Plant | g1 | TRUE
UtilFlty_ORFL_050 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Large Oil Refinery (>500,000 lb/day) | g1 | TRUE
UtilFlty_ORFM_051 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Medium Oil Refinery (100,000 - 500,000 lb/day) | g1 | TRUE
UtilFlty_ORFS_052 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Small Oil Refinery (< 100,000 lb/day) | g1 | TRUE
UtilFlty_OTF_053 | 0 | 0 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 0.0, 1.524: 0.0, 1.8288: 0.0, 2.1336: 0.0, 2.4384: 0.0, 2.7432: 0.0, 3.048: 0.0} | TRUE | TRUE | Oil Tank Farms | g1 | TRUE
UtilFlty_OCV_054 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 40.0, 0.6096: 40.0, 0.9144: 40.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Oil Control Vault and Control Stations | g1 | TRUE
UtilFlty_NGC_057 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Natural Gas Compressor Stations | g1 | TRUE
UtilFlty_NGCV_058 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 40.0, 0.6096: 40.0, 0.9144: 40.0, 1.2192: 40.0, 1.524: 40.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Natural Gas Control Valves and Control Stations | g1 | TRUE
UtilFlty_GDFLT_059 | 0 | 40 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 1.0, 0.6096: 2.0, 0.9144: 5.0, 1.2192: 15.0, 1.524: 30.0, 1.8288: 40.0, 2.1336: 40.0, 2.4384: 40.0, 2.7432: 40.0, 3.048: 40.0} | TRUE | TRUE | Natural Gas Default | g1 | TRUE
UtilFlty_EDFLT_060 | 0 | 0 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 0.0, 0.6096: 0.0, 0.9144: 0.0, 1.2192: 0.0, 1.524: 0.0, 1.8288: 0.0, 2.1336: 0.0, 2.4384: 0.0, 2.7432: 0.0, 3.048: 0.0} | TRUE | TRUE | Electric Power Default | g1 | TRUE
UtilFlty_EPPL_061 | 0 | 30 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.5, 0.6096: 5.0, 0.9144: 7.5, 1.2192: 10.0, 1.524: 12.5, 1.8288: 15.0, 2.1336: 17.5, 2.4384: 20.0, 2.7432: 25.0, 3.048: 30.0} | TRUE | TRUE | Electric Power Plant Large (>500 MW) | g1 | TRUE
UtilFlty_EPPM_062 | 0 | 30 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.5, 0.6096: 5.0, 0.9144: 7.5, 1.2192: 10.0, 1.524: 12.5, 1.8288: 15.0, 2.1336: 17.5, 2.4384: 20.0, 2.7432: 25.0, 3.048: 30.0} | TRUE | TRUE | Electric Power Plant Large (100-500 MW) | g1 | TRUE
UtilFlty_EPPS_063 | 0 | 30 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.5, 0.6096: 5.0, 0.9144: 7.5, 1.2192: 10.0, 1.524: 12.5, 1.8288: 15.0, 2.1336: 17.5, 2.4384: 20.0, 2.7432: 25.0, 3.048: 30.0} | TRUE | TRUE | Electric Power Plant Small (<100 MW) | g1 | TRUE
UtilFlty_ESSH_064 | 0 | 15 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.0, 0.6096: 4.0, 0.9144: 6.0, 1.2192: 7.0, 1.524: 8.0, 1.8288: 9.0, 2.1336: 10.0, 2.4384: 12.0, 2.7432: 14.0, 3.048: 15.0} | TRUE | TRUE | Substation - High Voltage (500 KV) | g1 | TRUE
UtilFlty_ESSM_065 | 0 | 15 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.0, 0.6096: 4.0, 0.9144: 6.0, 1.2192: 7.0, 1.524: 8.0, 1.8288: 9.0, 2.1336: 10.0, 2.4384: 12.0, 2.7432: 14.0, 3.048: 15.0} | TRUE | TRUE | Substation - Medium Voltage (230 KV) | g1 | TRUE
UtilFlty_ESSL_066 | 0 | 15 | [0.0, 0.3048, 0.6096, 0.9144, 1.2192, 1.524, 1.8288, 2.1336, 2.4384, 2.7432, 3.048] | {0.0: 0.0, 0.3048: 2.0, 0.6096: 4.0, 0.9144: 6.0, 1.2192: 7.0, 1.524: 8.0, 1.8288: 9.0, 2.1336: 10.0, 2.4384: 12.0, 2.7432: 14.0, 3.048: 15.0} | TRUE | TRUE | Substation - Low Voltage (115 KV) | g1 | TRUE

## UtilFlty_PDFLT_004
tag | UtilFlty_PDFLT_004
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PWTL_007
tag | UtilFlty_PWTL_007
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Some damage at ground level, most equipment assumed to be at 3ft in height
desc_asset | Large Gravity or Open Treatment Plant (> 200 MGD)
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_PWTM_008
tag | UtilFlty_PWTM_008
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Some damage at ground level, most equipment assumed to be at 3ft in height
desc_asset | Medium Gravity or Open Treatment Plant (50-200 MGD)
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_PWTS_009
tag | UtilFlty_PWTS_009
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Some damage at ground level, most equipment assumed to be at 3ft in height
desc_asset | Small Gravity or Open Treatment Plant (<50 MGD)
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_PWTO_010
tag | UtilFlty_PWTO_010
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Open Treatmet Plant Less than Average Damage (All)
exposure | impact
0 | 0
0.3048 | 3
0.6096 | 4
0.9144 | 5
1.2192 | 9
1.524 | 12
1.8288 | 15
2.1336 | 15
2.4384 | 15
2.7432 | 15
3.048 | 15

## UtilFlty_PWTO_011
tag | UtilFlty_PWTO_011
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Open Treatment Plant Greater than Average Damage (All)
exposure | impact
0 | 0
0.3048 | 8
0.6096 | 12
0.9144 | 15
1.2192 | 26
1.524 | 36
1.8288 | 45
2.1336 | 45
2.4384 | 45
2.7432 | 45
3.048 | 45

## UtilFlty_PWTL_012
tag | UtilFlty_PWTL_012
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment raised 3 feet above ground level
desc_asset | Large Closed or Pressure Treatment Plant (>200 MGD)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PWTM_013
tag | UtilFlty_PWTM_013
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment raised 3 feet above ground level
desc_asset | Medium Closed or Pressure Treatment Plant (50-200 MGD)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PWTS_014
tag | UtilFlty_PWTS_014
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment raised 3 feet above ground level
desc_asset | Small Closed or Pressure Treatment Plant (<50 MGD)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PWTC_015
tag | UtilFlty_PWTC_015
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Closed Treatment Plant Less than Average Damage (All)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 1
0.9144 | 3
1.2192 | 8
1.524 | 15
1.8288 | 20
2.1336 | 20
2.4384 | 20
2.7432 | 20
3.048 | 20

## UtilFlty_PWTC_016
tag | UtilFlty_PWTC_016
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Closed Treatment Plant Greater than Average Damage (All)
exposure | impact
0 | 0
0.3048 | 2
0.6096 | 3
0.9144 | 8
1.2192 | 23
1.524 | 45
1.8288 | 60
2.1336 | 60
2.4384 | 60
2.7432 | 60
3.048 | 60

## UtilFlty_PPPL_017
tag | UtilFlty_PPPL_017
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade
desc_asset | Large Pumping Plant Below Grade (>50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PPPM_018
tag | UtilFlty_PPPM_018
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade
desc_asset | Medium Pumping Plant Below Grade (10 - 50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PPPS_019
tag | UtilFlty_PPPS_019
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade
desc_asset | Small Pumping Plant Below Grade (<10 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PPPL_020
tag | UtilFlty_PPPL_020
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment raised 3 feet above ground level
desc_asset | Large Pumping Plant Above Grade (> 50MGD)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PPPM_021
tag | UtilFlty_PPPM_021
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment raised 3 feet above ground level
desc_asset | Medium Pumping Plant Above Grade (10 - 50 MGD)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PPPS_022
tag | UtilFlty_PPPS_022
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment raised 3 feet above ground level
desc_asset | Small Pumping Plant Above Grade (<10 MGD)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PCVS_023
tag | UtilFlty_PCVS_023
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance at grade and not sealed
desc_asset | Control Vaults and Control Stations
exposure | impact
0 | 0
0.3048 | 40
0.6096 | 40
0.9144 | 40
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_PSTAS_024
tag | UtilFlty_PSTAS_024
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Elevated Tanks
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 0
1.524 | 0
1.8288 | 0
2.1336 | 0
2.4384 | 0
2.7432 | 0
3.048 | 0

## UtilFlty_PSTBC_025
tag | UtilFlty_PSTBC_025
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Vent 3 feet above grade
desc_asset | Buried Concrete Tank
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 5
1.524 | 5
1.8288 | 5
2.1336 | 5
2.4384 | 5
2.7432 | 5
3.048 | 5

## UtilFlty_PSTGC_026
tag | UtilFlty_PSTGC_026
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Tank floor at grade and tank does not float
desc_asset | At Grade Concrete Tank
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 0
1.524 | 0
1.8288 | 0
2.1336 | 0
2.4384 | 0
2.7432 | 0
3.048 | 0

## UtilFlty_PSTGS_027
tag | UtilFlty_PSTGS_027
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Tank floor at grade and tank does not float
desc_asset | At Grade Steel Tank
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 0
1.524 | 0
1.8288 | 0
2.1336 | 0
2.4384 | 0
2.7432 | 0
3.048 | 0

## UtilFlty_PSTGW_028
tag | UtilFlty_PSTGW_028
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Tank floor at grade and tank does not float
desc_asset | At Grade Wood Tank
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 0
1.524 | 0
1.8288 | 0
2.1336 | 0
2.4384 | 0
2.7432 | 0
3.048 | 0

## UtilFlty_PWE_029
tag | UtilFlty_PWE_029
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Assumes electrical equipment and openings are 3ft above grade
desc_asset | Wells
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 20
1.524 | 25
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 30

## UtilFlty_WLSL_030
tag | UtilFlty_WLSL_030
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade and not sealed
desc_asset | Large Lift Station Dry Well (>50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WLSL_031
tag | UtilFlty_WLSL_031
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade and not sealed
desc_asset | Large Lift Station Wet Well (>50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WLSL_032
tag | UtilFlty_WLSL_032
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Water does not harm submersible pumps
desc_asset | Large Lift Station Submersible (>50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 10
1.524 | 10
1.8288 | 10
2.1336 | 10
2.4384 | 10
2.7432 | 10
3.048 | 10

## UtilFlty_WLSM_033
tag | UtilFlty_WLSM_033
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade and not sealed
desc_asset | Medium Lift Station Dry Well (10 - 50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WLSM_034
tag | UtilFlty_WLSM_034
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade and not sealed
desc_asset | Medium Lift Station Wet Well (10 - 50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WLSM_035
tag | UtilFlty_WLSM_035
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Water does not harm submersible pumps
desc_asset | Medium Lift Station Submersible (10 - 50 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 10
1.524 | 10
1.8288 | 10
2.1336 | 10
2.4384 | 10
2.7432 | 10
3.048 | 10

## UtilFlty_WLSS_036
tag | UtilFlty_WLSS_036
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade and not sealed
desc_asset | Small Lift Station Dry Well (<10 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WLSS_037
tag | UtilFlty_WLSS_037
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is 3 feet above grade and not sealed
desc_asset | Small Lift Station Wet Well (<10 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WLSS_038
tag | UtilFlty_WLSS_038
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Water does not harm submersible pumps
desc_asset | Small Lift Station Submersible (<10 MGD)
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 10
1.524 | 10
1.8288 | 10
2.1336 | 10
2.4384 | 10
2.7432 | 10
3.048 | 10

## UtilFlty_WWTL_039
tag | UtilFlty_WWTL_039
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Cleanup of small components when water exceeds grade, major electricl at 3ft above grade
desc_asset | Large Wastewater Treatment Plant (>200 MGD)
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_WWTA_040
tag | UtilFlty_WWTA_040
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Wastewater Treatment Plants Greater than Average Damage (All)
exposure | impact
0 | 0
0.3048 | 8
0.6096 | 12
0.9144 | 15
1.2192 | 26
1.524 | 36
1.8288 | 45
2.1336 | 45
2.4384 | 45
2.7432 | 45
3.048 | 60

## UtilFlty_WWTA_041
tag | UtilFlty_WWTA_041
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Wastewater Treatment Plants Less than Average Damage (All)
exposure | impact
0 | 0
0.3048 | 3
0.6096 | 4
0.9144 | 5
1.2192 | 9
1.524 | 12
1.8288 | 15
2.1336 | 15
2.4384 | 15
2.7432 | 15
3.048 | 20

## UtilFlty_WWTM_042
tag | UtilFlty_WWTM_042
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Cleanup of small components when water exceeds grade, major electricl at 3ft above grade
desc_asset | Medium Wastewater Treatment Plant (50 - 200 MGD)
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_WWTS_043
tag | UtilFlty_WWTS_043
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Cleanup of small components when water exceeds grade, major electricl at 3ft above grade
desc_asset | Small Wastewater Treatment Plant (<50 MGD)
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_WWCV_044
tag | UtilFlty_WWCV_044
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is at grade and not sealed
desc_asset | Wastewater Control Vaults and Control Stations
exposure | impact
0 | 0
0.3048 | 40
0.6096 | 40
0.9144 | 40
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_WDFLT_045
tag | UtilFlty_WDFLT_045
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Default Wastewater Facility
exposure | impact
0 | 0
0.3048 | 5
0.6096 | 8
0.9144 | 10
1.2192 | 17
1.524 | 24
1.8288 | 30
2.1336 | 30
2.4384 | 30
2.7432 | 30
3.048 | 40

## UtilFlty_ODFLT_048
tag | UtilFlty_ODFLT_048
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Default Oil Facility
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_OPP_049
tag | UtilFlty_OPP_049
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment is raised 3 feet above grade
desc_asset | Oil Pumping Plant
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_ORFL_050
tag | UtilFlty_ORFL_050
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment is raised 3 feet above grade
desc_asset | Large Oil Refinery (>500,000 lb/day)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_ORFM_051
tag | UtilFlty_ORFM_051
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment is raised 3 feet above grade
desc_asset | Medium Oil Refinery (100,000 - 500,000 lb/day)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_ORFS_052
tag | UtilFlty_ORFS_052
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | All equipment is raised 3 feet above grade
desc_asset | Small Oil Refinery (< 100,000 lb/day)
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_OTF_053
tag | UtilFlty_OTF_053
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Assume tank bottom is at grade and tanks will not float.
desc_asset | Oil Tank Farms
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 0
1.524 | 0
1.8288 | 0
2.1336 | 0
2.4384 | 0
2.7432 | 0
3.048 | 0

## UtilFlty_OCV_054
tag | UtilFlty_OCV_054
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is at grade and not sealed
desc_asset | Oil Control Vault and Control Stations
exposure | impact
0 | 0
0.3048 | 40
0.6096 | 40
0.9144 | 40
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_NGC_057
tag | UtilFlty_NGC_057
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Assumes Equipment is raised 3 ft.
desc_asset | Natural Gas Compressor Stations
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_NGCV_058
tag | UtilFlty_NGCV_058
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Entrance is at grade and not sealed
desc_asset | Natural Gas Control Valves and Control Stations
exposure | impact
0 | 0
0.3048 | 40
0.6096 | 40
0.9144 | 40
1.2192 | 40
1.524 | 40
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_GDFLT_059
tag | UtilFlty_GDFLT_059
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Natural Gas Default
exposure | impact
0 | 0
0.3048 | 1
0.6096 | 2
0.9144 | 5
1.2192 | 15
1.524 | 30
1.8288 | 40
2.1336 | 40
2.4384 | 40
2.7432 | 40
3.048 | 40

## UtilFlty_EDFLT_060
tag | UtilFlty_EDFLT_060
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Electric Power Default
exposure | impact
0 | 0
0.3048 | 0
0.6096 | 0
0.9144 | 0
1.2192 | 0
1.524 | 0
1.8288 | 0
2.1336 | 0
2.4384 | 0
2.7432 | 0
3.048 | 0

## UtilFlty_EPPL_061
tag | UtilFlty_EPPL_061
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Support facilities damaged at grade, control and generating facilities damaged at 2nd level
desc_asset | Electric Power Plant Large (>500 MW)
exposure | impact
0 | 0
0.3048 | 2.5
0.6096 | 5
0.9144 | 7.5
1.2192 | 10
1.524 | 12.5
1.8288 | 15
2.1336 | 17.5
2.4384 | 20
2.7432 | 25
3.048 | 30

## UtilFlty_EPPM_062
tag | UtilFlty_EPPM_062
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Support facilities damaged at grade, control and generating facilities damaged at 2nd level
desc_asset | Electric Power Plant Large (100-500 MW)
exposure | impact
0 | 0
0.3048 | 2.5
0.6096 | 5
0.9144 | 7.5
1.2192 | 10
1.524 | 12.5
1.8288 | 15
2.1336 | 17.5
2.4384 | 20
2.7432 | 25
3.048 | 30

## UtilFlty_EPPS_063
tag | UtilFlty_EPPS_063
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Support facilities damaged at grade, control and generating facilities damaged at 2nd level
desc_asset | Electric Power Plant Small (<100 MW)
exposure | impact
0 | 0
0.3048 | 2.5
0.6096 | 5
0.9144 | 7.5
1.2192 | 10
1.524 | 12.5
1.8288 | 15
2.1336 | 17.5
2.4384 | 20
2.7432 | 25
3.048 | 30

## UtilFlty_ESSH_064
tag | UtilFlty_ESSH_064
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment | Control room damaged at grade with max damage at 7ft,, incidental damage to transformers/switchgear
desc_asset | Substation - High Voltage (500 KV)
exposure | impact
0 | 0
0.3048 | 2
0.6096 | 4
0.9144 | 6
1.2192 | 7
1.524 | 8
1.8288 | 9
2.1336 | 10
2.4384 | 12
2.7432 | 14
3.048 | 15

## UtilFlty_ESSM_065
tag | UtilFlty_ESSM_065
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Substation - Medium Voltage (230 KV)
exposure | impact
0 | 0
0.3048 | 2
0.6096 | 4
0.9144 | 6
1.2192 | 7
1.524 | 8
1.8288 | 9
2.1336 | 10
2.4384 | 12
2.7432 | 14
3.048 | 15

## UtilFlty_ESSL_066
tag | UtilFlty_ESSL_066
desc | HAZUS builtin for buildings
source | Hazus Dflt, table='flUtilFlty' file=flDmRsFn.mdb received 2020-12-11
location | USA
date | ?
file_conversion | CanFlood.hazus_20210216
scale_units | monetary
impact_units | pct
exposure_units | meters
scale_var | replacement cost
exposure_var | flood depth above floor
impact_var | loss
comment
desc_asset | Substation - Low Voltage (115 KV)
exposure | impact
0 | 0
0.3048 | 2
0.6096 | 4
0.9144 | 6
1.2192 | 7
1.524 | 8
1.8288 | 9
2.1336 | 10
2.4384 | 12
2.7432 | 14
3.048 | 15